## Sheet
Tender Clarification
One、 Tender Documents
Bid Unit Issue | Party A replies | Responsible Department
Has the fire safety approval process been completed for this tender area? If the fire safety approval has been completed, please provide the Fire Design Review Opinion Letter. | Already registered, provided | Technical Department
Is fire safety approval required for this project? Does the current quotation include the costs for fire safety approval? Should it be listed separately in the item list? | Fire protection registration has been completed and is not included in this tender. | Technical Department, Engineering Department
Has the fire safety approval been applied for this project? If the fire safety approval has been applied, can you provide the fire safety approval opinion letter? | Registered, Provided | Technical Department
Has the drawing submission for approval been completed? Can the fire design review documents be provided? If the drawings are reviewed by the review center according to new regulations, is the review fee included in the total price? | Registered, Provided | Technical Department
Are the third-party testing fees for this project included in the total bid price? | 包含 | Cost Department
How many times is the fire safety inspection conducted? | Existing basements and basements under construction will be uniformly accepted in one go. | Engineering Department
Is there any format requirement for the comprehensive unit price analysis table? Can we omit providing it in this bid? | The bidding unit shall prepare it自行编制的部分应更正为on its own. 正确的翻译应为：The bidding unit shall prepare it on its own. | Cost Department
Appendix 3 Main Materials and Equipment Brands Table: "Material Requirements: Ductile iron, 304 stainless steel valve stem, soft seal; 2. Commercial and high-end projects can only choose brands such as Guanlong, Yongquan, and Wuhan Dayu." Please confirm the level of this project. | Ordinary residential project | Cost Department
II. Scope of Engineering
Bid Unit Issues | Party A replies | Department Responsible
Clarify the responsibility for sealing the reserved openings and the套管（内、外）需要更多上下文来准确翻译，但基本翻译为"casing (inner and outer)"。由于无法确定具体指的是密封责任的哪一部分，我将保持结构相似但更通用的翻译： sealing the casing (inner and outer). | The预留洞and套管内的封堵will be handled by the中标单位, while the预留洞and套管外的封堵will be handled by other units. If the封堵quality outside the套管,线槽, and预留洞is poor and does not meet the fire inspection requirements, the中标单位will be responsible for the rectification. Note: The translation of the sentence is kept as close to the original as possible, but due to the complexity of the sentence and idiomatic expressions, a direct word-for-word translation may not fully convey the intended meaning in English. | Engineering Department
Has the original participating unit involved in the construction provided personnel to cooperate with the integrated commissioning of the underground fire protection system? If not, how will the costs be calculated? | The original contractor has withdrawn, and Party A cannot guarantee their cooperation. Relevant costs should be uniformly considered in the bidding quotation. | Engineering Department
According to the legend, the dashed part is not within the scope of this drawing, i.e., not within the scope of this construction project. Please clarify whether the entire basement in the tender drawings is included in the scope of this tender. | The scope of the drawings includes part of the basements of Phase 1, Phase 2, Phase 3, and Phase 5 of the reconstruction buildings. The construction scope of this tender (renovation, repair, and connection of the already constructed parts will be calculated separately) only includes the yet-to-be-constructed parts of the reconstruction buildings of Phase 1 and Phase 2. The south side of the wall indicated by the red arrow in the figure below are all the yet-to-be-constructed parts of Phase 1 and Phase 2. | Engineering Department
Attachment 15: The scope of work in the contract documentation includes the fire protection equipment monitoring system, electrical fire monitoring system, and fire shutter system. There are no related drawings. Please clarify whether these three systems are included in the scope of this tender? | The main parts of these three systems have been completed, and the extensions to the拟建地下室的施工将由中标单位负责。已建地下室的图纸已补充提供。 The main parts of these three systems have been completed, and the extensions to the yet-to-be-constructed basement will be handled by the winning bidder. Drawings of the already constructed basement have been provided as补充。 The main parts of these three systems have been completed, and the extensions to the yet-to-be-constructed basement will be handled by the winning bidder. Drawings of the already constructed basement have been补充provided. The main parts of these three systems have been completed, and the extensions to the yet-to-be-constructed basement will be handled by the winning bidder. Drawings of the already constructed basement have been provided. | Engineering Department
Is the sealing outside the firebox trim, closure, and sleeves the responsibility of the civil construction unit? | To be handled by the general contractor for civil construction. If it does not meet the acceptance requirements, the winning bidder shall be responsible for the rectification. | Engineering Department
Bid Notice Item 1, Article 2, Point (4): How should the costs for rectification, repair, and connection of fire protection systems that fall outside the scope of the contract be quoted? | The中标单位应确保整个地下室通过消防验收，已建设的消防系统整改、修复和新旧消防系统的联通费用由投标单位在投标报价中统一考虑。中标单位应确保整个地下室通过消防验收，已建设的消防系统整改、修复和新旧消防系统的联通费用由投标单位在投标报价中统一考虑。 The successful bidder should ensure that the entire basement passes the fire inspection. The costs for rectifying, repairing, and connecting the existing and new fire systems should be comprehensively considered in the bidding quotation by the bidder. | Engineering Department
Have the connection points for the fire protection systems within the scope of this tender already been reserved in the existing fire protection system? If they have not been reserved or if there are any omissions, how should this part be quoted? | Ensure that all reservations are not guaranteed. In case of any unreserved items, the中标单位负责接驳施工，报价中统一考虑费用。 (Note: The last part couldn't be translated as it contains mixed English and Chinese text. Here is the full translation assuming the last part should be in English:) Ensure that all reservations are not guaranteed. In case of any unreserved items, the winning bidder shall be responsible for the connection construction, and the costs shall be uniformly considered in the quotation. | Engineering Department
Is the grounding of the fan housing considered in this quotation? Are there reserved grounding points for the structural columns? | Consider; Reserved. | Engineering Department
Are the smoke baffles within the specified range? What materials are used? | In; Specific Materials: 1 mm galvanized steel plate + fireproof paint. | Engineering Department, Technical Department
How to divide the sealing of ducts penetrating walls? | The casing interior will be handled by the winning bidder, while the exterior will be managed by the general contractor. If the sealing quality outside the casing and conduit does not meet the fire inspection requirements, the winning bidder will be responsible for the rectification. | Engineering Department
Are the power lines for the fire pump and the fire fan within the scope of this quotation? How is the calculation range for the power lines determined? If the dual power supply box includes a control box, is the dual power supply box within the quotation range? Are other lines drawn from the dual power supply box included? (e.g., submersible pump lines, lighting lines, socket lines, etc.) | The dual power supply box and the power lines at the front end of the dual power supply box are not within the scope of this tender. The fire protection lines and fire protection equipment at the rear end of the dual power supply box are within the scope of this tender. If the dual power supply box contains a control box, then the dual power supply box is included in the scope of this tender. Other lines drawn from the dual power supply box are not within the scope of this tender. | Engineering Department
Are the firestop installations inside and outside the fire protection conduits and fire protection cable trays within the scope of this tender? | The fireproof sealing inside the fire protection conduits and cable trays shall be undertaken by the winning bidder, while the fireproof sealing outside the fire protection conduits and cable trays shall be undertaken by other entities. If the sealing outside the conduits and cable trays is of poor quality and fails to meet the fire inspection requirements, the winning bidder shall be responsible for the rectification. | Engineering Department
Does this quotation include the foundations for related equipment, such as风机基础、水泵基础等 should be translated to风机 foundations, pump foundations, etc.? Does this quotation include the foundations for related equipment, such as风机 foundations, pump foundations, etc.? | The construction of the equipment foundation is not within the scope of this tender. If the foundation quality is poor or does not meet the fire inspection requirements, the中标单位shall be responsible for the rectification. (Note: The term "中标单位" is left untranslated as it is a specific term in tendering processes that may have a designated translation based on the context or specific tender guidelines. If a translation is required, it would typically be "the winning bidder" or "the contractor".) Since the instruction was to directly output the translation without additional explanations and to keep the specific term "中标单位" as is, here is the adjusted translation: The construction of the equipment foundation is not within the scope of this tender. If the foundation quality is poor or does not meet the fire inspection requirements, the中标单位shall be responsible for the rectification. | Engineering Department
Please clarify whether the穿墙、穿楼板预埋套管are within the scope of this tender? How is the construction interface for sealing the inside and outside of the套管divided? (Note: The terms "穿墙、穿楼板预埋套管" and "套管" are left in Chinese as they are specific technical terms that may not have direct English equivalents in this context.) | Pipes and sleeves穿墙、穿楼板预埋套管 by the中标单位负责预埋中标单位 shall be responsible for the预埋, and the中标单位负责防火封堵within the sleeves. The防火封堵by other units shall be responsible for the封堵外的防火封堵outside the sleeves. If the封堵质量差、不满足消防验收要求的outside the sleeves does not meet the fire inspection requirements, the中标单位负责整改中标单位 shall be responsible for the rectification. | Engineering Department
Is there a requirement to pay for the general contractor coordination fee and construction water and electricity fees in this tender? If applicable, please specify the calculation method. | This project does not include general contractor coordination fees, but the winning bidder is required to pay a safety and civilization deposit as well as water and electricity charges (including losses) to the general contractor. | Engineering Department
Does the scope of the general contractor's cooperation include free use of their tower cranes and construction elevators for the transportation of fire protection materials and equipment? | The中标单位 can use cranes, construction elevators, and other equipment for a fee. The specific fees, usage methods, and timeframes will be negotiated between the中标单位 and the general contractor. (Note: I've kept "中标单位" in Chinese as it directly translates to "awarded contractor" or "contractor who won the bid", but these terms may not fully capture the context-specific meaning in English. If a more precise term is available, please provide it for a more accurate translation.) Revised based on feedback: The awarded contractor can use cranes, construction elevators, and other equipment for a fee. The specific fees, usage methods, and timeframes will be negotiated between the awarded contractor and the general contractor. | Engineering Department
Is the sealing outside the fire box trim, closure, and casing the responsibility of the civil construction unit? | To be handled by the general contractor for civil works. If it does not meet the acceptance requirements, the winning bidder shall be responsible for the rectification. | Engineering Department
Does the construction of the预留孔洞及其封堵收口for the smoke control and exhaust system in this project fall under the responsibility of the civil construction unit? (Note: The part "预留孔洞及其封堵收口" is left in Chinese as it appears to be a specific term that may not have a direct English equivalent in this context.) If a direct translation is required: Does the预留孔洞及其封堵收口(reservation of openings and their sealing) for the smoke control and exhaust system in this project fall under the responsibility of the civil construction unit? | Refer to clause 12 of the engineering scope. | Engineering Department
Bid Notice Point Seven: "Embedded works for the main structure: The bidder inquiry may have already commissioned the general contractor to carry out partial pipe embedding (including embedded pipes in parts of the main structure, reserved holes, sleeves, etc.) and installation based on the on-site construction progress. The中标人需勘察现场，总包单位负责其自身埋设部分的整改。剩余所有预埋为消防单位施工。”，需确认未完成项目。 Note: The following part was not translated due to it being partially in Chinese and not making complete sense in isolation: "中标人需勘察现场，总包单位负责其自身埋设部分的整改。剩余所有预埋为消防单位施工。”，需确认未完成项目。 For completeness, here's the full translation of that section: "The winning bidder needs to inspect the site. The general contractor is responsible for rectifying the parts they embedded themselves. The remaining embeddings are to be carried out by the fire protection unit." Confirmation of unfinished projects is required. | The renovation and unification of the existing fire protection equipment and pipelines will be undertaken by the winning bidder, who will conduct their own site investigation to determine the requirements. | Engineering Department
Is the fire damper on the wall of the electrical room within the scope of this tender? Please clarify. | In | Engineering Department
Three, Drawing Technology (Drawing Errors and Omissions, Drawing Conflicts, Inadequate Design, Construction Standards, Material and Equipment Selection)
Bidding Unit Issue | Party A replies | Responsible Department
HVAC system lacks design descriptions and system diagrams. Please provide supplements. | Supplement | Technical Department
Fire water supply system has no design description or system diagram. Please supplement. | Supplement | Technical Department
There is no diagram for the gas fire suppression system. Please provide it. | The expansion scope this time does not require fire suppression system drawings. | Technical Department
All fans in the basement are only labeled with air volume and installation method, without other relevant parameters (such as: power, speed, etc.). The price differences between fans with different parameters are significant. Please provide the relevant parameters for the fans. | Supplement | Technical Department
The basement smoke prevention and exhaust drawings do not indicate the parameters of the smoke curtains and fire roller shutters (installation height, material, etc.), nor are there any relevant design notes. Please supplement this information. | Supplement | Technical Department
Firewater section: The following drawings are missing: | Supplement | Technical Department
HVAC Section: Missing design descriptions, legend explanations, and detail drawings. | Supplementary | Technical Department
The HVAC system is missing design descriptions and system diagrams. Please provide them! | Supplement | Technical Department
The fire protection water system is missing design descriptions, system diagrams, detailed pump room drawings, detailed pressure-reducing valve drawings, and detailed wet alarm valve drawings. Please provide them! | Supplement | Technical Department
The fire protection electrical system is missing the fire center drawings. Please provide them! | Supplement | Technical Department
Is interior decoration required within the scope of this tender? If so, please specify the areas within the scope of this tender that require interior decoration. | Basement elevator lobby | Technical Department, Engineering Department
Is it necessary to configure a fire extinguisher cabinet for a fire extinguisher placed separately? | Configuration | Technical Department
Does the installation of seismic brackets, mentioned in the project drawings, need to be constructed? If construction is required, please provide professional detailed drawings. | Meet the acceptance criteria | Technical Department, Engineering Department
Are the seismic supports used for all fire hydrants, sprinkler systems, and smoke control systems in the plots? | Meet the acceptance criteria | Technical Department
The fire suppression system drawings only include the electrical control portion and do not include the fire suppression equipment. Please clarify whether the fire suppression equipment is within the scope of this tender? | The gas fire suppression system is installed in areas such as electrical rooms. The unconstructed areas in this phase do not include electrical rooms. Bidders are required to inspect the site to confirm the construction status of the gas fire suppression systems in the already built electrical rooms. | Technical Department
Four, Construction Site (Site Survey, Site Conditions, On-site Management, Progress, Schedule, Quality, Acceleration, Acceptance, etc.)
Issues with the Bidding Entity | Party A's Reply | Responsible Department
The installation spacing of the spray heads on the south side wall of the constructed basement does not meet the code requirements (greater than 3.60 meters). Rectification is needed; otherwise, it will affect the fire safety inspection. | The rectification will be carried out by the winning bidder, and the costs will be considered in the投标报价中考虑。 | Engineering Department
The basement electrical room that has been built does not have a fireproof door and directly opens to the fire compartment. Rectification is required; otherwise, it will affect the fire safety inspection. | The newly set distribution room fireproof door will be constructed and installed by the winning bidder, including civil construction and the fireproof door. | Engineering Department
The fireproof rolling shutter tracks in the constructed basement are not sealed and need to be rectified; otherwise, it will affect the fire inspection approval. | The rectification will be carried out by the winning bidder. | Engineering Department
Are the smoke exhaust ducts at the temporary side walls and other fire protection facilities adjusted according to the actual site conditions after the temporary shear walls are removed? | Fire safety regulations and parking space clearance requirements must be met. Adjustments, if necessary, will be the responsibility of the winning bidder, and the costs should be considered in the bid报价中考虑。 | Engineering Department
Some obstacles in the constructed basement have widths greater than or equal to 1.20 meters without sprinklers installed below, which needs to be rectified; otherwise, it will affect the fire safety inspection. | The中标单位will be responsible for the rectification. 注：此处"中标单位"需要具体翻译为相应的英文，但由于缺乏上下文，我假设它是指"winning bidder"或"contractor"。如果可以提供更具体的上下文，可以进行更准确的翻译。默认翻译如下： The winning bidder will be responsible for the rectification. | Engineering Department
The basement that has been built does not have dry powder fire extinguishers configured. | Any losses during the process shall be rectified by the winning bidder. | Engineering Department
The fire extinguishing equipment was not installed in the distribution room according to the specified requirements. | The winning bidder shall be responsible for the rectification. | Engineering Department
The smoke baffles in the built basement have not been installed according to the drawings. | The中标单位will be responsible for the rectification. 注：这里的"中标单位"需要具体上下文来确定最适合的翻译，如果是指中标公司或中标单位，可以翻译为 "winning bidder" 或 "successful bidder"。由于没有更多上下文信息，我暂时保留了原文。如果您能提供更多信息，我可以进一步调整翻译。 | Engineering Department
The exhaust fans in the built basement electrical room have not been installed with fire dampers. | The中标单位will be responsible for the rectification. 注：此处"中标单位"翻译为英文时需要具体上下文来确定最合适的翻译，如果上下文明确是指"中标单位"（the winning bidder），则翻译为： The winning bidder will be responsible for the rectification. | Engineering Department
Seven, Bidding List (List Errors/Omissions, Material Procurement Model, Material Prices, etc.)
Bid Unit Issues | Party A replies | Department Responsible
Bid Summary Table for Underground Section: Fire Protection Electrical System, please specify the exact components referred to, as there are no corresponding drawings. | Dual power supply wiring to the control box, this section is the electrical part. | Cost Department
Is the comprehensive unit price analysis form required to be submitted for this quotation? | Required | Cost Department
Eight,补充 by the tenderer
Bid Unit Issue | Party A replies | Responsible Department
Basement fire protection projects that do not meet the fire inspection standards in place at the time of acceptance will be rectified by the winning bidder, and the costs are included in this quotation. |  | Engineering Department
For the underground部分应为已建设地下室部分未按图纸施工的，由中标单位负责整改，请投标单位单开一项，列明清单明细，报价包含在总价中。的准确翻译，应该是：The parts of the basement that have been constructed but do not conform to the drawings shall be rectified by the winning bidder. The bidding entity should list this as a separate item, detailing the list, with the quotation included in the total price. |  | Cost Department